DATA SHEET | PERFORMANCE DATA	6-CNFT-55 12V/55Ah

# the power of tomorrow

CLEAN ENERGY DEFINES THE WORLD THAT WE LIVE IN TODAY AND TOMORROW. LEAD CRYSTAL® TECHNOLOGY CREATES POWER THAT IS CLEAN SAFE AND

## HIGH PERFORMING FOR A BETTER FUTURE

| SPECIFICATION |  |  |
| --- | --- | --- |
| Nominal Voltage | 12V |  |
| Rated Capacity (10 hour rate) | 55 AH |  |
| Dimension Total Height (top of terminal) | 225 mm | 8.86" |
| Height | 222 mm | 8.74" |
| Length | 277 mm | 10.90" |
| Width | 106 mm | 4.17" |

DISCHARGE CURRENT AND END VOLTAGE

Weight	Approximately

16.8kg / 37.03 lbs

Discharge current (A)

0.05C or below or Intermittent discharge 0.05C of current close to it

0.1C of current close to it 0.2C of current close to it From 0.2C to 0.5C

From 0.5C to 1C From 1C to 3C

Current in excess of 3C

End voltage (V) 11.4

11.1

10.8

10.5

10.2

9.6

9.0

7.8

Capacity 25ºC

Internal Resistance

Self-Discharge 25ºC

120 hour rate (0.55A) 20 hour rate (3.0A) 10 hour rate (5.5A)

Fully charged Battery (25ºC)

Capacity after 3 month storage Capacity after 6 month storage Capacity after 12 month storage

66 AH

60 AH

55 AH

8m0

95%

85%

80%

CHARGE vs TEMPERATURE

VOLTAGE/CELL

VOLTAGE/CELL

2.7

2.6

2.5

2.4

2.3

2.2

2.1

2

CYCLE CHARGE FLOAT CHARGE

| Terminal | Standard F3 |
| --- | --- |
|  | Optional |
| Charging (Constant Voltage) | Initial Charging Cycle Current 16.5A 14.7V/ (25℃) |
|  | Float 13.6V/ (25℃) |

Max Discharge Current 25ºC

550A (5S)

-40 -35 -30 -25 -20 -15 -10 -5 0

TEMPERATURE (°C)

5 10 15 20 25 30 35  40 45 50 55 60 65 70

CHARGE vs TEMPERATURE CHART

| temperature | -40 | -35 | -30 -25 -20 -15 | -10 -5 | 0 5 | 10 | 15 20 25 30 35 40 45 50 |  | 55 60 | 65 70 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cycle Charge | 2.66 2.64 2.62 2.60 2.58 2.56 |  |  | 2.54 2.52 2.50 2.48 |  | 2.47 2.47 |  | 2.45 2.45 2.43 2.41 2.39 2.37 2.35 2.33 2.31 |  | 2.29 2.27 |
| Float Charge (voltage/cell) | 2.46 2.44 2.42 2.40 2.38 2.36 |  |  | 2.34 2.32 2.31 2.30 |  | 2.29 2.29 |  | 2.29 2.27 2.26 2.24 2.23 2.23 2.23 2.23 2.23 |  | 2.23 2.23 |

CONSTANT CURRENT DISCHARGE CHARACTERISTICS: UNITS AMPERES (25°C)

| End Voltage per cell | 5min 15min 30min 45min | 1h 2h 3h 4h | 5h | 6h | 8h | 10h | 12h | 20h | 24h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1.60V | 201.83 106.81 64.54 47.05 | 37.90 21.71 15.77 12.37 | 10.55 | 8.97 | 6.84 | 5.69 | 4.78 | 3.11 | 2.54 |
| 1.67V | 187.57 103.31 63.58 46.73 | 37.83 21.62 15.48 12.30 | 10.40 | 8.90 | 6.83 | 5.63 | 4.77 | 3.10 | 2.53 |
| 1.70V | 185.66 101.73 62.94 46.10 | 37.52 21.43 15.39 12.24 | 10.24 | 8.81 | 6.80 | 5.63 | 4.75 | 3.09 | 2.53 |
| 1.75V | 170.08 98.54 62.32 45.78 | 36.88 21.01 15.32 12.08 | 10.14 | 8.74 | 6.77 | 5.56 | 4.73 | 3.08 | 2.52 |
| 1.80V | 152.59 92.18 59.76 44.51 | 35.92 20.70 15.26 12.05 | 10.01 | 8.65 | 6.74 | 5.50 | 4.71 | 2.97 | 2.52 |
| 1.83V | 145.86 84.57 58.82 42.92 | 34.34 20.51 14.66 11.54 | 9.79 | 8.33 | 6.60 | 5.28 | 4.51 | 2.94 | 2.49 |
| 1.85V | 136.69 82.02 55.00 41.33 | 33.38 19.68 14.27 11.38 | 9.54 | 8.05 | 6.52 | 5.21 | 4.45 | 2.91 | 2.46 |

DISCHARGE DATA WITH CONSTANT POWER UNITS: WATTS PER CELL (25°C)

| End Voltage per cell | 5min 15min 30min 45min 1h 2h 3h 4h | 5h | 6h | 8h | 10h | 12h | 20h | 24h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1.60V | 337.26 187.55 120.79 88.05 70.83 41.01 29.98 23.75 | 20.06 | 17.23 | 13.29 | 11.00 | 9.25 | 6.17 | 5.05 |
| 1.67V | 321.05 184.69 115.91 87.42 70.89 41.01 29.59 23.71 | 20.06 | 17.20 | 13.29 | 10.97 | 9.25 | 6.17 | 5.05 |
| 1.70V | 319.14 183.41 115.85 87.42 70.25 40.69 29.53 23.63 | 19.74 | 17.07 | 13.19 | 10.87 | 9.15 | 6.13 | 5.05 |
| 1.75V | 297.21 181.19 115.98 87.42 69.93 40.37 29.47 23.59 | 19.68 | 16.94 | 13.13 | 10.80 | 9.15 | 6.13 | 5.02 |
| 1.80V | 272.74 171.97 113.48 85.83 69.62 40.37 29.44 23.52 | 19.55 | 16.94 | 13.10 | 10.74 | 9.15 | 5.98 | 5.02 |
| 1.83V | 263.20 157.98 112.53 83.28 66.75 40.05 28.61 22.73 | 19.33 | 16.40 | 13.10 | 10.43 | 9.00 | 5.91 | 4.99 |
| 1.85V | 243.81 154.49 104.58 80.11 64.85 39.10 27.81 22.44 | 18.79 | 16.08 | 12.59 | 10.33 | 8.84 | 5.85 | 4.96 |

6-CNFT-55 12V/55Ah

CYCLE CHARGE CHARACTERISTIC (25°C)	FLOATING CHARGE CHARACTERISTIC (25°C)

REGULAR CYCLE CHARGE CHARACTERISTICS 77°F (25°C)	FLOATING CHARGE CHARACTERISTICS 77°F (25°C)

CHARGE CHARGING CHARGING

CHARGE CHARGING CHARGING

CAPACITY CURRENT

VOLTAGE

CAPACITY CURRENT

VOLTAGE

(%)

120

100

80

60

40

20

0

(CA)

0.30

0.24

0.18

0.12

0.06

0.00

(V)

CHARGING VOLTAGE

CHARGE CAPACITY

CHARGING CURRENT

CHARGING VOLTAGE

CHARGE CAPACITY

CHARGING CURRENT

14.7

13.6

12.3

11.1

0	3	6	9	12	15	18

TIME (H)

(%)

110

100

80

60

40

20

0

(CA)

0.10

0.08

0.06

0.04

0.02

0.00

(V)

CHARGING VOLTAGE

CHARGE CAPACITY

CHARGING CURRENT

CHARGING VOLTAGE

CHARGE CAPACITY

CHARGING CURRENT

14.0

13.2

12.4

11.6

10.8

0	5	10	15	20	25	30

TIME (H)

CAPACITY RATE (%)

CAPACITY RATE (%)

CYCLE LIFE CURVE GRAPH

CAPACITY RATE (%)

CAPACITY RATE (%)

CYCLE LIFE CURVE GRAPH ( 2 5 °C)

NUMBER OF CYCLES

CYCLE LIFE CURVE GRAPH ( 4 0 °C)

NUMBER OF CYCLES

TEMPERATURE & FLOAT SERVICE LIFE	FLOAT SERVICE LIFE CURVE GRAPH

CAPACITY RATE (%)

CAPACITY RATE (%)

100

90

80

70

60

50

40

30

|  | 60 | ºC | 5 | 0ºC |  |  | 40ºC |  |  | 25ºC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

0	1	2	3	4	5	6	7	8	9	10	11

SERVICE LIFE YEAR (YEAR)

TEMPERATURE & DISCHARGE CAPACITY

22

20

18

16

14

LIFE (YEAR)

LIFE (YEAR)

12

10

8

6

4

2

0

0	10	20	30	40	50	60

TEMPERATURE (°C)

DISCHARGE RATIO ( %)

DISCHARGE RATIO ( %)

120

100

80

60

40

20

0

40	30	20	10	0	10	20	30	40  50	60

TEMPERATURE (°C)

0.05CA

  - CA

  - CA

0.5CA

6-CNFT-55 12V/55Ah

LEAD CRYSTAL®:

CHANGING THE FUTURE

Performance Robust, resilient, high performing. Lead Crystal® batteries can be discharged deeper, cycled more often (also in extreme temperatures) and have a longer service life. They recover to full rated capacity over and over again.

Technology A unique micro-porous high absorbent mat (AGM), high-purity lead calcium selenium plates, safe SiO2 electrolyte solution that solidifies into a white crystalline powder when charged/discharged.

Cleaner & safe Less acid, no cadmium, no antimony. Lead Crystal® batteries are up to 99% recyclable and are classified as non-hazardous goods for transport.

Markets Lead Crystal® batteries are being used in telecoms, ups, petrochem/marine, defence, renewable energy, health care, manufacturing, transportation and electric motion (wheelchairs, golf carts & trolleys).

https:// leadcrystaltechnologies.com